## Slide 1
GEF a grant of 50 Million US$ to cover a substantial part of the incremental cost in comparison to the least cost conventional alternative producing the same annual amount of the electric energy.
JBIC a soft loan to finance the thermal portion of the plant by about 10.665 + 6.44 Billion JPY.
NREA will cover the local currency portion required for the project
Financing the Project

## Slide 2
Project Description
The plant will have a capacity of about 140 MWe, out of them from solar sources of about 20 MWe combining with a conventional fossil fuel portion of about 120 MW.
The solar island consists of a parabolic trough solar field with total area about 130800 m2 capable of generating about 147 GWhth/a of solar heat at a temperature of 393°C, the related Instrumentation and Control (I&C) and control room and the heat transfer fluid (HTF) system .
The combined cycle island will consist of one gas turbine with ISO rating of about 79 MWe, one heat recovery steam generator (HRSG), one steam turbine of about 76.5 MWe, and solar heat exchanger capable to absorb about the solar heat, plus all associated balance of plant equipment.

## Slide 3
Technical Design
600
°
C
Gas turbine(s)
Steam
turbine
Condenser
Steam
540
°
C, 100bar
Stack Exhaust
100
°
C
395
°
C
Electricity
to the grid
Parabolic
Trough Field
295
°
C
Gas turbine(s)
Steam
turbine
Condenser
Steam
540
°
C, 100bar
Stack Exhaust
100
°
C
395
°
C
Electricity
to the grid
Parabolic
Trough Field
295
°
C
Tower
G
~
Solar HX
Solar Island
600
°
C
Gas turbine(s)
Steam
turbine
Condenser
Steam
540
°
C, 100bar
Stack Exhaust
100
°
C
395
°
C
Electricity
to the grid
Parabolic
Trough Field
295
°
C
Air and
vapour
Air
Air
G ~
HRSG
Cooling
Tower
G
~
G
~
G
~
Solar HX
Solar Island
CC Island
Integrated Solar Combined Cycle Power Plant “ISCCS”

## Slide 4
Summary of Technical Parameters | 
20 | Capacity of solar portion (MWe)
131 | Solar collectors area (1000 m2)
79 | Nameplate capacity of gas turbine (MWe)
76.5 | Nameplate capacity of steam turbine (MWe)
852 | Net electric energy (GWhe/a)
33 | Solar electric energy (GWhe/a)
4% | Solar share(%)
10000 | Fuel saving due to the solar portion (T.O.E / a)
20000 | CO2 reduction (T/a)
Project Technical Parameters
Notes: 4

## Slide 5
Project Construction

## Slide 6
Project Construction